## Sc3
year | total_energy_requirement (MWh) | Energy Fulfilment Ratio (%) | Critical Load Interruptions | Estimated Loss due to Interruptions | Non-critical Load shedding events | Total Cost (M $) | Unit Cost ($/kWh) | Existing Solar PPA Total Energy Output (MWh) | Existing Solar PPA Total Cost of Operation (M $) | Existing Solar PPA Unit Cost ($/kWh) | PPA based on Solar plant source Total Energy Output (MWh) | PPA based on Solar plant source Total Cost of Operation (M $) | PPA based on Solar plant source Unit Cost ($/kWh) | PPA based on BESS Total Energy Output (MWh) | PPA based on BESS Total Cost of Operation (M $) | PPA based on BESS Unit Cost ($/kWh) | Captive DG Sets Total Energy Output (MWh) | Captive DG Sets Total Cost of Operation (M $) | Captive DG Sets Unit Cost ($/kWh)
1 | 42357.15 | 100 | 1 | 0.08 | 4 | 8.36 | 0.2 | 5571.09 | 0.21 | 0.04 | 31517.14 | 2.76 | 0.09 | 23220.32 | 4.08 | 0.18 | 4259.62 | 1.23 | 0.29
2 | 42357.15 | 100 | 0 | 0 | 5 | 8.28 | 0.2 | 5569.64 | 0.21 | 0.04 | 31575.19 | 2.76 | 0.09 | 23217.84 | 4.08 | 0.18 | 4273.46 | 1.23 | 0.29
3 | 45382.66 | 100 | 0 | 0 | 4 | 8.94 | 0.2 | 5585.42 | 0.21 | 0.04 | 34588.18 | 3.1 | 0.09 | 25051.48 | 4.42 | 0.18 | 4212.78 | 1.21 | 0.29
4 | 45382.66 | 100 | 0 | 0 | 4 | 8.93 | 0.2 | 5585.29 | 0.21 | 0.04 | 34547.15 | 3.1 | 0.09 | 25012.27 | 4.42 | 0.18 | 4193.67 | 1.2 | 0.29
5 | 49618.38 | 100 | 0 | 0 | 5 | 9.99 | 0.2 | 5548.18 | 0.21 | 0.04 | 38668.18 | 3.46 | 0.09 | 27740.17 | 5.1 | 0.18 | 4246.42 | 1.22 | 0.29
6 | 49618.38 | 100 | 0 | 0 | 6 | 9.99 | 0.2 | 5549.72 | 0.21 | 0.04 | 38602.28 | 3.46 | 0.09 | 27743.03 | 5.1 | 0.18 | 4258.21 | 1.22 | 0.29
7 | 49618.38 | 100 | 0 | 0 | 6 | 9.99 | 0.2 | 5548.18 | 0.21 | 0.04 | 38689.56 | 3.46 | 0.09 | 27706.75 | 5.1 | 0.18 | 4251.2 | 1.22 | 0.29
8 | 54459.19 | 100 | 0 | 0 | 4 | 11.13 | 0.2 | 5524.34 | 0.21 | 0.04 | 42962.25 | 3.82 | 0.09 | 30439.04 | 5.78 | 0.19 | 4681.34 | 1.32 | 0.28
9 | 54459.19 | 100 | 0 | 0 | 3 | 11.14 | 0.2 | 5525.56 | 0.21 | 0.04 | 42981.12 | 3.82 | 0.09 | 30425.78 | 5.78 | 0.19 | 4692.54 | 1.33 | 0.28
10 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5526.62 | 0.21 | 0.04 | 43107.54 | 3.82 | 0.09 | 30699.41 | 6.46 | 0.21 | 4529.67 | 1.29 | 0.28
11 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5602.35 | 0.21 | 0.04 | 45019.18 | 3.84 | 0.09 | 32142.47 | 6.46 | 0.2 | 5388.91 | 1.54 | 0.29
12 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5598.46 | 0.21 | 0.04 | 44960.09 | 3.84 | 0.09 | 32132.7 | 6.46 | 0.2 | 5416.38 | 1.54 | 0.28
| Existing Solar |  | 5 | MW
| Diesel Generator |  | 6 | No.
Solar PV PPA
|  |  | 40 | MW | from year 1
|  |  | 5 | MW | from year 3
|  |  | 5 | MW | from year 5
|  |  | 5 | MW | from year 8
BESS PPA
|  |  | 60 | MWh | from year 1
|  |  | 5 | MWh | from year 3
|  |  | 10 | MWh | from year 5
|  |  | 10 | MWh | from year 8
|  |  | 10 | MWh | from year 10

## Sc3Deck
Year | Energy Requirement (MWh) | Energy Fulfilment Ratio (%) | Critical Load Interruptions | Estimated Loss due to Interruptions | Non-critical Load shedding events | Total Cost (M $) | Unit Cost ($/kWh) | Existing Solar PPA Energy Output (MWh) | Existing Solar PPA Cost of Operation (M $) | Existing Solar PPA Unit Cost ($/kWh) | New Solar PPA Energy Output (MWh) | New Solar PPA Cost of Operation (M $) | New Solar PPA Unit Cost ($/kWh) | BESS PPA Energy Output (MWh) | BESS PPA Cost of Operation (M $) | BESS PPA Unit Cost ($/kWh) | DG Sets Energy Output (MWh) | DG Sets Cost of Operation (M $) | DG Sets Unit Cost ($/kWh) | Existing Solar PPA | New Solar PPA | Captive DG Sets | BESS PPA
1 | 42357.15 | 100 | 1 | 0.08 | 4 | 8.36 | 0.2 | 5571.09 | 0.21 | 0.04 | 31517.14 | 2.76 | 0.09 | 23220.32 | 4.08 | 0.18 | 4259.62 | 1.23 | 0.29 | 66.7349 | 467.2179 | 54.4042
2 | 42357.15 | 100 | 0 | 0 | 5 | 8.28 | 0.2 | 5569.64 | 0.21 | 0.04 | 31575.19 | 2.76 | 0.09 | 23217.84 | 4.08 | 0.18 | 4273.46 | 1.23 | 0.29 | 2.52 | 41.24 | 15.55 | 63.24
3 | 45382.66 | 100 | 0 | 0 | 4 | 8.94 | 0.2 | 5585.42 | 0.21 | 0.04 | 34588.18 | 3.1 | 0.09 | 25051.48 | 4.42 | 0.18 | 4212.78 | 1.21 | 0.29
4 | 45382.66 | 100 | 0 | 0 | 4 | 8.93 | 0.2 | 5585.29 | 0.21 | 0.04 | 34547.15 | 3.1 | 0.09 | 25012.27 | 4.42 | 0.18 | 4193.67 | 1.2 | 0.29
5 | 49618.38 | 100 | 0 | 0 | 5 | 9.99 | 0.2 | 5548.18 | 0.21 | 0.04 | 38668.18 | 3.46 | 0.09 | 27740.17 | 5.1 | 0.18 | 4246.42 | 1.22 | 0.29
6 | 49618.38 | 100 | 0 | 0 | 6 | 9.99 | 0.2 | 5549.72 | 0.21 | 0.04 | 38602.28 | 3.46 | 0.09 | 27743.03 | 5.1 | 0.18 | 4258.21 | 1.22 | 0.29
7 | 49618.38 | 100 | 0 | 0 | 6 | 9.99 | 0.2 | 5548.18 | 0.21 | 0.04 | 38689.56 | 3.46 | 0.09 | 27706.75 | 5.1 | 0.18 | 4251.2 | 1.22 | 0.29
8 | 54459.19 | 100 | 0 | 0 | 4 | 11.13 | 0.2 | 5524.34 | 0.21 | 0.04 | 42962.25 | 3.82 | 0.09 | 30439.04 | 5.78 | 0.19 | 4681.34 | 1.32 | 0.28
9 | 54459.19 | 100 | 0 | 0 | 3 | 11.14 | 0.2 | 5525.56 | 0.21 | 0.04 | 42981.12 | 3.82 | 0.09 | 30425.78 | 5.78 | 0.19 | 4692.54 | 1.33 | 0.28
10 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5526.62 | 0.21 | 0.04 | 43107.54 | 3.82 | 0.09 | 30699.41 | 6.46 | 0.21 | 4529.67 | 1.29 | 0.28
11 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5602.35 | 0.21 | 0.04 | 45019.18 | 3.84 | 0.09 | 32142.47 | 6.46 | 0.2 | 5388.91 | 1.54 | 0.29
12 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5598.46 | 0.21 | 0.04 | 44960.09 | 3.84 | 0.09 | 32132.7 | 6.46 | 0.2 | 5416.38 | 1.54 | 0.28

## Sc2
Year | Energy Requirement (MWh) | Energy Fulfilment Ratio (%) | Critical Load Interruptions | Estimated Loss due to Interruptions | Non-critical Load shedding events | Total Cost (M $) | Unit Cost ($/kWh) | Existing Solar PPA Energy Output (MWh) | Existing Solar PPA Cost of Operation (M $) | Existing Solar PPA Unit Cost ($/kWh) | New Solar PPA Energy Output (MWh) | New Solar PPA Cost of Operation (M $) | New Solar PPA Unit Cost ($/kWh) | BESS PPA Energy Output (MWh) | BESS PPA Cost of Operation (M $) | BESS PPA Unit Cost ($/kWh) | DG Sets Energy Output (MWh) | DG Sets Cost of Operation (M $) | DG Sets Unit Cost ($/kWh)
1 | 42357.15 | 100 | 0 | 0 | 0 | 11.11 | 0.26 | 5444.48 | 0.21 | 0.04 | 33817.8 | 3.78 | 0.11 | 23913.13 | 6.46 | 0.27 | 2289.49 | 0.66 | 0.29
2 | 42357.15 | 100 | 0 | 0 | 0 | 11.11 | 0.26 | 5450.87 | 0.21 | 0.04 | 33805.22 | 3.78 | 0.11 | 23903.16 | 6.46 | 0.27 | 2273.07 | 0.66 | 0.29
3 | 45382.66 | 100 | 0 | 0 | 0 | 11.23 | 0.25 | 5499.88 | 0.21 | 0.04 | 36313.26 | 3.78 | 0.1 | 25758.5 | 6.46 | 0.25 | 2651.15 | 0.78 | 0.29
4 | 45382.66 | 100 | 0 | 0 | 0 | 11.23 | 0.25 | 5518.23 | 0.21 | 0.04 | 36296.77 | 3.78 | 0.1 | 25737.13 | 6.46 | 0.25 | 2640.84 | 0.78 | 0.3
5 | 49618.38 | 100 | 0 | 0 | 0 | 11.45 | 0.23 | 5520.68 | 0.21 | 0.04 | 39629.74 | 3.79 | 0.1 | 28244.15 | 6.46 | 0.23 | 3399.13 | 0.99 | 0.29
6 | 49618.38 | 100 | 0 | 0 | 0 | 11.45 | 0.23 | 5519.97 | 0.21 | 0.04 | 39627.88 | 3.79 | 0.1 | 28246.23 | 6.46 | 0.23 | 3398.16 | 0.99 | 0.29
7 | 49618.38 | 100 | 0 | 0 | 0 | 11.45 | 0.23 | 5510.66 | 0.21 | 0.04 | 39631.66 | 3.79 | 0.1 | 28225.81 | 6.46 | 0.23 | 3391.6 | 0.99 | 0.29
8 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5520.15 | 0.21 | 0.04 | 43081.38 | 3.82 | 0.09 | 30715.65 | 6.46 | 0.21 | 4530.24 | 1.29 | 0.28
9 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5524.81 | 0.21 | 0.04 | 43097.46 | 3.82 | 0.09 | 30711.44 | 6.46 | 0.21 | 4562.57 | 1.29 | 0.28
10 | 54459.19 | 100 | 0 | 0 | 3 | 11.78 | 0.22 | 5527.16 | 0.21 | 0.04 | 43105.47 | 3.82 | 0.09 | 30712.27 | 6.46 | 0.21 | 4537.49 | 1.29 | 0.28
11 | 57484.7 | 100 | 0 | 0 | 4 | 12.05 | 0.21 | 5596.43 | 0.21 | 0.04 | 44979.98 | 3.83 | 0.09 | 32117.75 | 6.46 | 0.2 | 5405.29 | 1.55 | 0.29
12 | 57484.7 | 100 | 0 | 0 | 3 | 12.05 | 0.21 | 5593.52 | 0.21 | 0.04 | 45010.47 | 3.84 | 0.09 | 32129.77 | 6.46 | 0.2 | 5410.16 | 1.54 | 0.28
[20 empty] | Year | Energy Requirement as % of Year 12 requirement | Total Energy Cost as % of Year 12 Cost
| Existing Solar |  | 5 | MW | [15 empty] | 1 | 73.6842 | 92.1992
| Solar PV PPA |  | 55 | MW | from year 1 | [14 empty] | 2 | 73.6842 | 92.1992
| BESS PPA |  | 95 | MWh | from year 1 | [14 empty] | 3 | 78.9474 | 93.195
| Diesel Generator |  | 6 | No. | [15 empty] | 4 | 78.9474 | 93.195
[20 empty] | 5 | 86.3158 | 95.0207
[20 empty] | 6 | 86.3158 | 95.0207
[20 empty] | 7 | 86.3158 | 95.0207
[20 empty] | 8 | 94.7368 | 97.7593
[20 empty] | 9 | 94.7368 | 97.7593
[20 empty] | 10 | 94.7368 | 97.7593
[20 empty] | 11 | 100 | 100
[20 empty] | 12 | 100 | 100

## Sc1
Year | Energy Requirement (MWh) | Energy Fulfilment Ratio (%) | Critical Load Interruptions | Estimated Loss due to Interruptions | Non-critical Load shedding events | Total Cost (M $) | Unit Cost ($/kWh) | Existing Solar PPA Energy Output (MWh) | Existing Solar PPA Cost of Operation (M $) | Existing Solar PPA Unit Cost ($/kWh) | New Solar PPA Energy Output (MWh) | New Solar PPA Cost of Operation (M $) | New Solar PPA Unit Cost ($/kWh) | BESS PPA Energy Output (MWh) | BESS PPA Cost of Operation (M $) | BESS PPA Unit Cost ($/kWh) | DG Sets Energy Output (MWh) | DG Sets Cost of Operation (M $) | DG Sets Unit Cost ($/kWh)
1 | 42357.15 | 100 | 1 | 0.08 | 7 | 13.51 | 0.32 | 5777.26 | 0.22 | 0.04 | 26273.14 | 1.81 | 0.07 | 23932.1 | 8.97 | 0.37 | 8675.87 | 2.43 | 0.28
2 | 42357.15 | 100 | 1 | 0.08 | 10 | 13.51 | 0.32 | 5785.32 | 0.22 | 0.04 | 26315.25 | 1.82 | 0.07 | 23952.5 | 8.97 | 0.37 | 8664.67 | 2.42 | 0.28
3 | 45382.66 | 100 | 1 | 0.08 | 24 | 14.2 | 0.31 | 5820.98 | 0.22 | 0.04 | 27000.39 | 1.87 | 0.07 | 24704.91 | 8.97 | 0.36 | 10952.78 | 3.06 | 0.28
4 | 45382.66 | 100 | 1 | 0.08 | 20 | 14.19 | 0.31 | 5828.96 | 0.22 | 0.04 | 26961.26 | 1.86 | 0.07 | 24754.33 | 8.97 | 0.36 | 10965.51 | 3.06 | 0.28
5 | 49618.38 | 100 | 4 | 0.33 | 39 | 15.44 | 0.31 | 5836.37 | 0.22 | 0.04 | 27674.83 | 1.91 | 0.07 | 25265.91 | 8.97 | 0.36 | 14508.01 | 4.01 | 0.28
6 | 49618.38 | 99.99 | 2 | 0.17 | 42 | 15.31 | 0.31 | 5836.03 | 0.22 | 0.04 | 27669.55 | 1.91 | 0.07 | 25247.11 | 8.97 | 0.36 | 14571.72 | 4.04 | 0.28
7 | 49618.38 | 99.99 | 6 | 0.5 | 40 | 15.62 | 0.31 | 5827.86 | 0.22 | 0.04 | 27641.15 | 1.91 | 0.07 | 25223.98 | 8.97 | 0.36 | 14526.55 | 4.02 | 0.28
8 | 54459.19 | 99.93 | 11 | 0.91 | 57 | 17.3 | 0.32 | 5843.33 | 0.22 | 0.04 | 28068.48 | 1.92 | 0.07 | 24689.03 | 8.97 | 0.36 | 19115.05 | 5.28 | 0.28
9 | 54459.19 | 99.89 | 13 | 1.08 | 55 | 17.46 | 0.32 | 5836.73 | 0.22 | 0.04 | 28035.36 | 1.93 | 0.07 | 24615.67 | 8.97 | 0.36 | 19105.81 | 5.26 | 0.28
10 | 54459.19 | 99.92 | 9 | 0.74 | 62 | 17.14 | 0.31 | 5841.13 | 0.22 | 0.04 | 28071.41 | 1.94 | 0.07 | 24619.82 | 8.97 | 0.36 | 19108.71 | 5.27 | 0.28
11 | 57484.7 | 99.61 | 36 | 2.98 | 84 | 20.22 | 0.35 | 5850.33 | 0.22 | 0.04 | 28163.73 | 1.94 | 0.07 | 23663.4 | 8.97 | 0.38 | 22138.15 | 6.11 | 0.28
12 | 57484.7 | 99.54 | 43 | 3.56 | 82 | 20.79 | 0.36 | 5855.78 | 0.22 | 0.04 | 28181.02 | 1.94 | 0.07 | 23609.47 | 8.97 | 0.38 | 22109.25 | 6.1 | 0.28
[8 empty] | 69940.08 |  |  | 330055.57 | [5 empty] | 184442.08
| Existing Solar |  | 5 | MW
| Solar PV PPA |  | 35 | MW | from year 1
| BESS PPA |  | 130 | MWh | from year 1
| Diesel Generator |  | 6 | No.
[20 empty] | Existing Solar PPA Energy Output (MWh) | New Solar PPA Energy Output (MWh) | DG Sets Energy Output (MWh)
[20 empty] | 69940.08 | 330055.57 | 184442.08

## solar profile
Jan | 279
Feb | 278.2
Mar | 251.8
Apr | 269.2
May | 256.2
Jun | 197.8
Jul | 156.4
Aug | 183.6
Sep | 223.6
Oct | 262.2
Nov | 279
Dec | 307

## sc table
No. | Scenario Description | Critical Load Interrupts. | Non-critical load shed events | Avg Cost ($/kWh) | Total Cost for 12 years (M$) | Notes
1 | a. Existing PV Plant – 5 MW b. 35MW New PV Plant from Year 1 c. 130 MWh BESS d. 6 x 1.5MW HSD from Year 1 | 128 | 522 | 0.321 | 194.69 | This scenario has a high number of critical load interruptions as well as excessive Diesel generator use. Both are due to to inadequate solar output to charge BESS, especially during the rainy season. When BESS is discharged, sudden reductions in solar output (which are routine) cannot be handled by the system, thus causing critical load interruptions. Secondly, since PV is undersized to meet the BESS charging requirements, the gap is filled filled by diesel generators which naturally pushes the costs up.
2 | a. Existing PV Plant – 5 MW b. 55MW New PV Plant from Year 1 c. 95 MWh BESS d. 6 x 1.5MW HSD from Year 1 | 0 | 52 | 0.233 | 138.47 | Learning from Scenario 1, sizes of BESS and PV plant are now balanced. This leads to low consumption of diesel generators. Since BESS is adequately charged, sudden reduction in solar outputs can be handled seamlessly. However both PV and BESS capacities are excessive, especially up till Year 6 which leads to under utilization and higher unit costs.
3 | a. Existing PV Plant – 5 MW b. New PV Plant (Total 55 MW): - 40 MW (Year 1) - 5 MW (Year 3) - 5 MW (Year 5) - 5 MW (Year 8) c. BESS (Total 95 MWh) - 60MWh (Year 1) - 5MWh (Year 3) - 10MWh (Year 5) - 10MWh (Year 8) - 10MWh ( Year 10) d. 6 x 1.5MW HSD from Year 1 | 0 | 52 | 0.203 | 122.63 | This scenario optimizes Scenario 2 by adding both PV and BESS capacity in phased manner, aligned with the projected demand. Staged addition of PPA sources prevents underutilization. Also as seen in Scenario 2, higher ratio of PV to BESS capacities ensures that the vast majority of energy used to charge BESS comes from PV and not diesel. This helps in keep unit costs low.